## register_mapping
Field_name | Label | Ordinal | Register_number
X | colnames(log_data)
datetime | DateTime
X003A | HWB_SOC_pct | 58 | input_registers,58
X003B | HWB_SOC_KJ | 59 | input_registers,59
X003C |  | 60 | input_registers,60
X003D | CHB_SOC_pct | 61 | input_registers,61
X003E | CHB_SOC_KJ | 62 | input_registers,62
X003F |  | 63 | input_registers,63
X0001 | HS_TS1 | 1 | input_registers,1
X0002 | HS_TS2 | 2 | input_registers,2
X0003 | HS_TS3 | 3 | input_registers,3
X0004 | HS_TS4 | 4 | input_registers,4
X0005 | HS_TS5 | 5 | input_registers,5
X0006 | HS_TS6 | 6 | input_registers,6
X0007 | HS_TS7 | 7 | input_registers,7
X0008 | HS_TS8 | 8 | input_registers,8
X0009 | HS_TS9 | 9 | input_registers,9
X000A | HS_TS10 | 10 | input_registers,10
X000B | HS_TS11 | 11 | input_registers,11
X000C | HS_TS12 | 12 | input_registers,12
X000D | HS_TS13 | 13 | input_registers,13
X000E | HP_TS14 | 14 | input_registers,14
X000F | HP_TS15 | 15 | input_registers,15
X0010 | HP_TS16 | 16 | input_registers,16
X0011 | HP_TS17 | 17 | input_registers,17
X0012 | HP_TS18 | 18 | input_registers,18
X0013 | ROOM_TS19 | 19 | input_registers,19
X0014 | HWB_TSB | 20 | input_registers,20
X0015 | HWB_TSM | 21 | input_registers,21
X0016 | HWB_TST | 22 | input_registers,22
X0017 | CHB_TS1_1 | 23 | input_registers,23
X0018 | CHB_TS1_2 | 24 | input_registers,24
X0019 | CHB_TS1_3 | 25 | input_registers,25
X001A | CHB_TS1_4 | 26 | input_registers,26
X001B | CHB_TS1_5 | 27 | input_registers,27
X001C |  | 28 | input_registers,28
X001D | CHB_TS2_1 | 29 | input_registers,29
X001E | CHB_TS2_2 | 30 | input_registers,30
X001F | CHB_TS2_3 | 31 | input_registers,31
X0020 | CHB_TS2_4 | 32 | input_registers,32
X0021 | CHB_TS2_5 | 33 | input_registers,33
X0022 |  | 34 | input_registers,34
X0023 | CHB_TS3_1 | 35 | input_registers,35
X0024 | CHB_TS3_2 | 36 | input_registers,36
X0025 | CHB_TS3_3 | 37 | input_registers,37
X0026 | CHB_TS3_4 | 38 | input_registers,38
X0027 | CHB_TS3_5 | 39 | input_registers,39
X0028 |  | 40 | input_registers,40
X0029 |  | 41 | input_registers,41
X002A | CHB_TS4_1 | 42 | input_registers,42
X002B | CHB_TS4_2 | 43 | input_registers,43
X002C | CHB_TS4_3 | 44 | input_registers,44
X002D | CHB_TS4_4 | 45 | input_registers,45
X002E | CHB_TS4_5 | 46 | input_registers,46
X002F | CHB_TS5_1 | 47 | input_registers,47
X0030 | CHB_TS5_2 | 48 | input_registers,48
X0031 | CHB_TS5_3 | 49 | input_registers,49
X0032 | CHB_TS5_4 | 50 | input_registers,50
X0033 | CHB_TS5_5 | 51 | input_registers,51
X0034 | CHB_TS6_1 | 52 | input_registers,52
X0035 | CHB_TS6_2 | 53 | input_registers,53
X0036 | CHB_TS6_3 | 54 | input_registers,54
X0037 | CHB_TS6_4 | 55 | input_registers,55
X0038 | CHB_TS6_5 | 56 | input_registers,56
X0039 |  | 57 | input_registers,57
X0040 | FS1_FS | 64 | input_registers,64
X0041 | FS2_FS | 65 | input_registers,65
X0042 | FS3_FS | 66 | input_registers,66
X0043 | FS4_FS | 67 | input_registers,67
X0044 | FS5_FS | 68 | input_registers,68
X0045 | FS6_FS | 69 | input_registers,69
X0046 | FS7_FS | 70 | input_registers,70
X0047 | FS8_FS | 71 | input_registers,71
X0048 | FS1_TS | 72 | input_registers,72
X0049 | FS2_TS | 73 | input_registers,73
X004A | FS3_TS | 74 | input_registers,74
X004B | FS4_TS | 75 | input_registers,75
X004C | FS5_TS | 76 | input_registers,76
X004D | FS6_TS | 77 | input_registers,77
X004E | FS7_TS | 78 | input_registers,78
X004F | FS8_TS | 79 | input_registers,79
X0050 | PS1 | 80 | input_registers,80
X0051 | PS2 | 81 | input_registers,81
X0052 | PS3 | 82 | input_registers,82
X0053 | PS4 | 83 | input_registers,83
X0054 | PM1_I | 84 | input_registers,84
X0055 |  | 85 | input_registers,85
X0056 | PM1_W | 86 | input_registers,86
X0057 |  | 87 | input_registers,87
X0058 | PM1_PVA | 88 | input_registers,88
X0059 |  | 89 | input_registers,89
X005A | PM1_PWH | 90 | input_registers,90
X005B |  | 91 | input_registers,91
X005C | PM1_FR | 92 | input_registers,92
X005D | PM1_PF | 93 | input_registers,93
X005E | PM1_V | 94 | input_registers,94
X005F | PM2_I | 95 | input_registers,95
X0060 |  | 96 | input_registers,96
X0061 | PM2_PW | 97 | input_registers,97
X0062 |  | 98 | input_registers,98
X0063 | PM2_PVA | 99 | input_registers,99
X0064 |  | 100 | input_registers,100
X0065 | PM2_PWH | 101 | input_registers,101
X0066 |  | 102 | input_registers,102
X0067 | PM2_FR | 103 | input_registers,103
X0068 | PM2_PF | 104 | input_registers,104
X0069 | PM2_V | 105 | input_registers,105
X006A | PM3_I | 106 | input_registers,106
X006B |  | 107 | input_registers,107
X006C | PM3_PW | 108 | input_registers,108
X006D |  | 109 | input_registers,109
X006E | PM3_PVA | 110 | input_registers,110
X006F |  | 111 | input_registers,111
X0070 | PM3_PWH | 112 | input_registers,112
X0071 |  | 113 | input_registers,113
X0072 | PM3_FR | 114 | input_registers,114
X0073 | PM3_PF | 115 | input_registers,115
X0074 | PM3_V | 116 | input_registers,116
X0075 | PM4_I | 117 | input_registers,117
X0076 |  | 118 | input_registers,118
X0077 | PM4_PW | 119 | input_registers,119
X0078 |  | 120 | input_registers,120
X0079 | PM4_PVA | 121 | input_registers,121
X007A |  | 122 | input_registers,122
X007B | PM4_PWH | 123 | input_registers,123
X007C |  | 124 | input_registers,124
X007D | PM4_FR | 125 | input_registers,125
X007E | PM4_PF | 126 | input_registers,126
X007F | PM4_V | 127 | input_registers,127
X0080 | DV1 | 128 | input_registers,128
X0081 | DV2 | 129 | input_registers,129
X0082 | DV3 | 130 | input_registers,130
X0083 | DV4 | 131 | input_registers,131
X0084 | DV5 | 132 | input_registers,132
X0085 | DV6 | 133 | input_registers,133
X0086 | DV7 | 134 | input_registers,134
X0087 | DV8 | 135 | input_registers,135
X0088 | MV1 | 136 | input_registers,136
X0089 | MV2 | 137 | input_registers,137
X008A | MV3 | 138 | input_registers,138
X008B | PUMP_1 | 139 | input_registers,139
X008C | PUMP_2 | 140 | input_registers,140
X008D | PUMP_3 | 141 | input_registers,141
X008F | SYS_CURR_OPM | 143 | input_registers,143
X0090 | 32-bits: Heat meter Power x 100 | 144 | input_registers,144
X0091 |  | 142 | input_registers,142
X0092 |  | 145 | input_registers,145
X0093 |  | 146 | input_registers,146
X0094 |  | 147 | input_registers,147
X0095 |  | 148 | input_registers,148
| discrete_registers,1 |  | discrete_registers,1
| discrete_registers,2 |  | discrete_registers,2

## Info
Field_name | Label | Mapping | Label | Data type | Units
colnames(log_data) | colnames(log_data) | NULL
datetime | DateTime | DateTime |  | DateTime | DateTime
003A | HWB_SOC_% | HWB_SOC: in % State of charge in Thermino battery |  | int | % SOC
003B | HWB_SOC_KJ | HWB_SOC in KJ x 100 |  | int | KJ x100
003D | CHB_SOC_% | CHB_SOC: in % State of charge in CH battery |  | int | % SOC
003E | CHB_SOC_KJ | CHB_SOC in KJ x 100 |  | int | KJ x100
1 | HS_TS1 | HS_TS1: Hydronic System |  | int | Temp*100
2 | HS_TS2 | HS_TS2: Hydronic System |  | int | Temp*100
3 | HS_TS3 | HS_TS3: Hydronic System |  | int | Temp*100
4 | HS_TS4 | HS_TS4: Hydronic System |  | int | Temp*100
5 | HS_TS5 | HS_TS5: Hydronic System |  | int | Temp*100
6 | HS_TS6 | HS_TS6: Hydronic System |  | int | Temp*100
7 | HS_TS7 | HS_TS7: Hydronic System |  | int | Temp*100
8 | HS_TS8 | HS_TS8: Hydronic System |  | int | Temp*100
9 | HS_TS9 | HS_TS9: Hydronic System |  | int | Temp*100
000A | HS_TS10 | HS_TS10: Hydronic System |  | int | Temp*100
000B | HS_TS11 | HS_TS11: Hydronic System |  | int | Temp*100
000C | HS_TS12 | HS_TS12: Hydronic System |  | int | Temp*100
000D | HS_TS13 | HS_TS13: Hydronic System |  | int | Temp*100
000E | HP_TS14 | HP_TS14: HP System |  | int | Temp*100
000F | HP_TS15 | HP_TS15: HP System |  | int | Temp*100
10 | HP_TS16 | HP_TS16: HP System |  | int | Temp*100
11 | HP_TS17 | HP_TS17: HP System |  | int | Temp*100
12 | HP_TS18 | HP_TS18: HP System |  | int | Temp*100
13 | ROOM_TS19 | ROOM_TS19: Room temperature (B: 3988) |  |  | Temp*100
14 | HWB_TSB | HWB_TSB: Bottom temperature sensor (TS1) |  |  | Temp*100
15 | HWB _TSM | HWB _TSM: Middle temperature sensor (TS2) |  |  | Temp*100
16 | HWB _TST | HWB _TST: Top temperature sensor (TS3) |  |  | Temp*100
17 | CHB_TS1_1 | CHB_TS1 | 1 |  | Temp*100
18 | CHB_TS1_2 | CHB_TS2 | 2 |  | Temp*100
19 | CHB_TS1_3 | CHB_TS3 | 3 |  | Temp*100
001A | CHB_TS1_4 | CHB_TS4 | 4 |  | Temp*100
001B | CHB_TS1_5 | CHB_TS5 | 5 |  | Temp*100
001C | CHB_TS2_1 | CHB_TS6 | 1 |  | Temp*100
001D | CHB_TS2_2 | CHB_TS7 | 2 |  | Temp*100
001E | CHB_TS2_3 | CHB_TS8 | 3 |  | Temp*100
001F | CHB_TS2_4 | CHB_TS9 | 4 |  | Temp*100
20 | CHB_TS2_5 | CHB_TS10 | 5 |  | Temp*100
21 | CHB_TS3_1 | CHB_TS11 | 1 |  | Temp*100
22 | CHB_TS3_2 | CHB_TS12 | 2 |  | Temp*100
23 | CHB_TS3_3 | CHB_TS13 | 3 |  | Temp*100
24 | CHB_TS3_4 | CHB_TS14 | 4 |  | Temp*100
25 | CHB_TS3_5 | CHB_TS15 | 5 |  | Temp*100
26 | CHB_TS4_1 | CHB_TS16 | 1 |  | Temp*100
27 | CHB_TS4_2 | CHB_TS17 | 2 |  | Temp*100
28 | CHB_TS4_3 | CHB_TS18 | 3 |  | Temp*100
29 | CHB_TS4_4 | CHB_TS19 | 4 |  | Temp*100
002A | CHB_TS4_5 | CHB_TS20 | 5 |  | Temp*100
002B | CHB_TS5_1 | CHB_TS21 | 1 |  | Temp*100
002C | CHB_TS5_2 | CHB_TS22 | 2 |  | Temp*100
002D | CHB_TS5_3 | CHB_TS23 | 3 |  | Temp*100
002E | CHB_TS5_4 | CHB_TS24 | 4 |  | Temp*100
002F | CHB_TS5_5 | CHB_TS25 | 5 |  | Temp*100
30 | CHB_TS6_1 | CHB_TS26 | 1 |  | Temp*100
31 | CHB_TS6_2 | CHB_TS27 | 2 |  | Temp*100
32 | CHB_TS6_3 | CHB_TS28 | 3 |  | Temp*100
33 | CHB_TS6_4 | CHB_TS29 | 4 |  | Temp*100
34 | CHB_TS6_5 | CHB_TS30 | 5 |  | Temp*100
35 | CHB_TS7_1 | CHB_TS31 | 1 |  | Temp*100
36 | CHB_TS7_2 | CHB_TS32 | 2 |  | Temp*100
37 | CHB_TS7_3 | CHB_TS33 | 3 |  | Temp*100
38 | CHB_TS7_4 | CHB_TS34 | 4 |  | Temp*100
39 | CHB_TS7_5 | CHB_TS35 | 5 |  | Temp*100
40 | FS1_FS | FS1_FS |  |  | l/min*100
41 | FS2_FS | FS2_FS |  |  | l/min*100
42 | FS3_FS | FS3_FS |  |  | l/min*100
43 | FS4_FS | FS4_FS |  |  | l/min*100
44 | FS5_FS | FS5_FS |  |  | l/min*100
45 | FS6_FS | FS6_FS |  |  | l/min*100
46 | FS7_FS | FS7_FS |  |  | l/min*100
47 | FS8_FS | FS8_FS |  |  | l/min*100
48 | FS1_TS | FS1_TS |  |  | l/min*100
49 | FS2_TS | FS2_TS |  |  | l/min*100
004A | FS3_TS | FS3_TS |  |  | l/min*100
004B | FS4_TS | FS4_TS |  |  | l/min*100
004C | FS5_TS | FS5_TS |  |  | l/min*100
004D | FS6_TS | FS6_TS |  |  | l/min*100
004E | FS7_TS | FS7_TS |  |  | l/min*100
004F | FS8_TS | FS8_TS |  |  | l/min*100
50 | PS1 | PS1 |  |  | bar*100
51 | PS2 | PS2 |  |  | bar*100
52 | PS3 | PS3 |  |  | bar*100
53 | PS4 | PS4 |  |  | bar*100
54 | PM1_I | I: 32-bit Current in A x 1000 | HP
55 |  |  |  |  | BLANK
56 | PM1_W | PW: 32-bit Power in W | HP
57 |  |  |  |  | BLANK
58 | PM1_PVA | PVA: 32-bit Power in VA | HP
59 |  |  |  |  | BLANK
005A | PM1_PWH | PWH: 32-bit kWh accumulated | HP
005B |  |  |  |  | BLANK
005C | PM1_FR | FR: 16-bit Frequency x 10 | HP
005D | PM1_PF | PF: 16-bit PF x 1000 | HP
005E | PM1_V | V:16-bit Voltage x 10 | HP
005F | PM2_I | I: 32-bit Current in A x 1000 | Electric Boiler
60 |  |  |  |  | BLANK
61 | PM2_PW | PW: 32-bit Power in W | Electric Boiler
62 |  |  |  |  | BLANK
63 | PM2_PVA | PVA: 32-bit Power in VA | Electric Boiler
64 |  |  |  |  | BLANK
65 | PM2_PWH | PWH: 32-bit kWh accumulated | Electric Boiler
66 |  |  |  |  | BLANK
67 | PM2_FR | FR: 16-bit Frequency x 10 | Electric Boiler
68 | PM2_PF | PF: 16-bit PF x 1000 | Electric Boiler
69 | PM2_V | V:16-bit Voltage x 10 | Electric Boiler
006A | PM3_I | I: 32-bit Current in A x 1000 | Thermino
006B |  | BLANK | BLANK
006C | PM3_PW | PW: 32-bit Power in W | Thermino
006D |  |  |  |  | BLANK
006E | PM3_PVA | PVA: 32-bit Power in VA | Thermino
006F |  |  |  |  | BLANK
70 | PM3_PWH | PWH: 32-bit kWh accumulated | Thermino
71 |  |  |  |  | BLANK
72 | PM3_FR | FR: 16-bit Frequency x 10 | Thermino
73 | PM3_PF | PF: 16-bit PF x 1000
74 | PM3_V | V:16-bit Voltage x 10 | Thermino
75 | PM4_I | I: 32-bit Current in A x 1000 | PM 4
76 |  |  |  |  | BLANK
77 | PM4_PW | PW: 32-bit Power in W | PM4
78
79 | PM4_PVA | PVA: 32-bit Power in VA | PM4
007A |  |  |  |  | BLANK
007B | PM4_PWH | PWH: 32-bit kWh accumulated | PM4
007C |  |  |  |  | BLANK
007D | PM4_FR | FR: 16-bit Frequency x 10 | PM4
007E | PM4_PF | PF: 16-bit PF x 1000 | PM4
007F | PM4_V | V:16-bit Voltage x 10 | PM4
80 | DV1 | DV1
81 | DV2 | DV2
82 | DV3 | DV3
83 | DV4 | DV4
84 | DV5 | DV5
85 | DV6 | DV6
86 | DV7 | DV7
87 | DV8 | DV8
88 | MV1 | MV1
89 | MV2 | MV2
008A | MV3 | MV3
008B | PUMP_1 | PUMP_1
008C | PUMP_2 | PUMP_2
008D | PUMP_3 | PUMP_3
008F | SYS_CURR_OPM: the running OPM | SYS_CURR_OPM: the running OPM
90 | 32-bits: Heat meter Power x 100 | 32-bits: Heat meter Power x 100
91 |  |  |  |  | BLANK
92 |  | ERROR REGISTER 1
93 |  | ERROR REGISTER 2
94 |  | ERROR REGISTER 3

## Op_mode
Reading | State | Explination
0 | O1 | Idle
1 | A1 | Space Heating From Heat Pump with AU as HP source
2 | A2 | EXTEND Heat Battery Charging From Heat Pump with AU as source
4 | A3 | Thermino Charging from Heat Pump with AU as source
10 | S1 | Space Heating from EXTEND Heat Battery
40 | D1 | EXTEND Heat Battery Electrical Element Operation (1, 2 or 3 elements in operation, modulating element always the 1st)
80 | D2 | Thermino Electrical Element Operation
21 | S2A1 | Space Heating from HP with EXTEND HB as source
41 | D1A1 | Space Heating from HP with AU as source and charge EXTEND HB with element(s)
44 | D1A3 | Charge Thermino from HP with AU as source and charge EXTEND HB with element(s)
50 | D1S1 | Space Heating from EXTEND HB and EXTEND element operation
81 | D2A1 | Space Heating From HP with AU as source and charging Thermino with Thermino element
82 | D2A2 | EXTEND HB Charging From HP with AU as source and charging Thermino with Thermino element
84 | D2A3 | Thermino Charging from Heat Pump with AU as source and charging Thermino with Thermino element
90 | D2S1 | Space Heating from EXTEND Heat Battery and charging Thermino with Thermino element
A1 | D2S2A1 | Space Heating from HP with EXTEND HB as source and charging Thermino with Thermino element
C0 | D2D1 | EXTEND Heat Battery Electrical Element Operation and charging Thermino with Thermino element
100 | DF1 | Defrost from EXTEND Heat Battery
200 | DF2 | Defrost from Space Heating
180 | DF1D2 | Thermino Electrical Element Operation and Defrost from EXTEND Heat Battery
240 | DF2D1 | EXTEND Heat Battery Electrical Element Operation and Defrost from Space Heating
280 | DF2D2 | Thermino Electrical Element Operation and Defrost from Space Heating
400 | FP0 | Passive frost protection
800 | FP1 | Active frost protection
8001 | PA1 | Passive Space Heating From Heat Pump with AU as HP source
8010 | PS1 | Passive Space Heating from EXTEND Heat Battery
8021 | PS2A1 | Space Heating from HP with EXTEND HB as source
8041 | PD1A1 | Passive Space Heating from HP with AU as source and charge EXTEND HB with element(s)
8050 | PD1S1 | Passive Space Heating from EXTEND HB and EXTEND element operation
8081 | PD2A1 | Passive Space Heating From HP with AU as source and charging Thermino with Thermino element
8090 | PD2S1 | Passive Space Heating from EXTEND Heat Battery and charging Thermino with Thermino element
80A1 | PD2S2A1 | Passive Space Heating from HP with EXTEND HB as source and charging Thermino with Thermino element
1000 | FL1 | Flushing
FFFF | ERR | Error mode – need an engineer visit
A000 | STR | System just restarted
ffff | ERR | Error mode – need an engineer visit
80a1 | PD2S2A1 | Passive Space Heating from HP with EXTEND HB as source and charging Thermino with Thermino element
a000 | STR | System just restarted
a1 | D2S2A1 | Space Heating from HP with EXTEND HB as source and charging Thermino with Thermino element
8 | C0 | Commissioning (Idle)
9 | C1 | Commissioning (Nitrogen Purge)
000A | C2 | Commissioning (Fill prep)
000B | C3 | Commissioning (Flushing)